Final

Stormwater Pollution Prevention Plan

City of Appleton

Wastewater Treatment Plant

2006 East Newberry Street

Appleton, WI  54911

Prepared for the:

City of Appleton

100 N. Appleton Street

Appleton, WI  54911

Prepared by:

Earth Tech, Inc.

1020 N. Broadway, Suite 400

Milwaukee, WI  53202

June 2005

Updated January 6, 2017

(By Appleton Utilities)

STORMWATER POLLUTION PREVENTION PLAN

CITY OF APPLETON

WASTEWATER TREATMENT PLANT

2006 E. NEWBERRY STREET

APPLETON, WI  54911

Prepared for:

City of Appleton

100 N. Appleton Street

Appleton, WI  54911

June 6, 2005

Updated January 6, 2017

(By Appleton Utilities)

Earth Tech, Inc.

Kelly S. Mattfield, P.E.

Senior Engineer

TABLE OF CONTENTS

Page

STATEMENT OF CERTIFICATION	1

1.	introduction	1-1

1.1	Site Description	1-1

1.2	Regulatory Background	1-1

1.3	Objectives and Scope of Stormwater Pollution Prevention Plan	1-1

1.4	Stormwater Pollution Prevention Responsibility	1-2

1.5	Plan Availability	1-2

1.6	Plan Compliance and Modifications	1-3

1.7	Previously Developed Stormwater Management Plans	1-3

2.	Stormwater pollution prevention team	2-1

2.1	Team Coordinator	2-1

2.2	Team Members	2-1

3.	potential contamination sources and risk identification	3-1

3.1	Initial Site Evaluation Summary	3-1

3.2	Stormwater Drainage and Outfalls	3-2

3.3	Areas of Potential Stormwater Contamination	3-3

3.3.1	Asphalt Drives and Parking Areas	3-3

3.3.2	Refuse and Recycling Containers	3-3

3.3.3	Fuel Oil and Gasoline Storage Tanks	3-3

3.3.4	Equipment and Material Storage Areas	3-4

3.3.5	Electrical Substation	3-4

3.3.6	Sewage Unloading Areas	3-4

3.3.7	Chemical Unloading Areas	3-5

3.4	Materials Inventory	3-5

3.5	Historical Leaks and Spills	3-5

4.	non-stormwater discharges	4-1

5.	BEST MANAGEMENT PRACTICES	5-1

5.1	Objective	5-1

5.2	Measures and Controls	5-1

5.2.1	Existing BMPs	5-1

5.2.2	Proposed BMPs (Updated to Existing BMPs)	5-2

5.3	Best Management Practices Implementation	5-2

5.4	Prohibited Activities	5-4

5.5	Residual Pollutants Expected to Remain in Stormwater	5-4

5.6	Stormwater Treatment Practices	5-4

6.	inspections and recordkeeping	6-1

6.1	Quarterly Visual Stormwater Inspections	6-1

6.2	Annual Site Inspection	6-1

6.3	Semi-Annual Dry Weather Inspection	6-1

6.4	Spill Management and Documentation	6-1

6.5	Annual Stormwater Sampling and Testing	6-2

6.6	SWMP Updates or Revisions	6-2

6.7	Employee Training Requirements	6-2

6.8	Preventive Maintenance	6-3

6.9	Implementation Schedule	6-3

7.	references	7-1

LIST OF TABLES

Table 	Page

1	Stormwater Pollution Prevention Team	2-2

2	Stormwater Areas and Activity Inventory	3-2

3	Materials Inventory	3-6

4	Recommended Best Management Practices	5-3

5	SWPPP Implementation Schedule	6-3

LIST OF FIGURES

Figure

1	Site Location Map

2	Wastewater Treatment Facility Layout and Drainage Map

LIST OF APPENDICES

Appendix

A	Stormwater Permit

B	Blank Checklists and Forms

Quarterly Visual Stormwater Inspection

Non-Stormwater Discharges

Annual Site Inspection Checklist

Spill Documentation Form

Employee Training Record

C	Completed Checklists and Forms

D	WDNR Fact Sheet Defining Reportable Spills

# STATEMENT OF CERTIFICATION

According to NR 216.29(8), all reports required under this subchapter require signature.  The following "Statement of Certification" is identical to the statement on WDNR Form 3400-167 "Stormwater Management Plan Summary".

“I certify under penalty of law that this document and attachments were prepared under my direction or supervision in accordance with a system designed to ensure that qualified personnel properly gathered and evaluated the information contained in the plan.  Based on my inquiry of the person or persons who manage the system, or those persons directly responsible for gathering the information, the information in this document is, to the best of my knowledge and belief, true, accurate and complete.  I am aware that there are significant penalties for submitting false information, including the possibility of fine and imprisonment for knowing violations.  In addition, I certify under penalty of law that, based upon inquiry of persons directly under my supervision, to the best of my knowledge and belief, the provisions of this document adhere to the provisions of the stormwater permit for development and implementation of a Stormwater Management Plan and that the plan will be complied with.”

Authorized Signature:

Chris Shaw  							Date

Utilities Director

City of Appleton

2006 East Newberry Street

Appleton, WI  54911

# introduction

## Site Description

The Appleton Wastewater Treatment Plant (WWTP) is located at 2006 East Newberry Street, Appleton, Wisconsin, in the NE ¼ of Section 30 of Township 21 North, Range 18 East, Outagamie County, Wisconsin.  The WWTP is on the south side of the Fox River approximately 1 mile west of State Highway 441.  The location of the WWTP is shown on Figure 1.

The WWTP is bounded by the Fox River to the north, Newberry Street to the south, and residential areas to the east and west.  The entire WWTP site encompasses approximately 43 acres.  The WWTP layout is shown on Figure 2.

## Regulatory Background

The United States Environmental Protection Agency (USEPA) developed the stormwater regulatory program through the authority of the Clean Water Act amendments of 1987, to reduce discharges of contaminated stormwater associated with industrial facilities.  The National Pollutant Discharge Elimination System (NPDES) program is the means that the USEPA regulates discharges of potentially contaminated wastewater and stormwater into Waters of the United States through the issuance of permits applicable to specific sources.

The Federal Clean Water Act of 1972 and rules adopted by the USEPA require permits for stormwater discharges where precipitation and/or stormwater runoff come into contact with contaminants through industrial activity, at construction sites, or from municipal areas.  The philosophy for implementing the permit requirements emphasizes pollution prevention, which provides substantial environmental benefit with minimum regulatory burden.

In Wisconsin, the Department of Natural Resources (WDNR) is the permitting authority for the Stormwater NPDES program.  Stormwater regulations are located in Chapter NR 216 of the Wisconsin Administrative Code.  All code references cited in this Stormwater Pollution Prevention Plan (SWPPP) refer to current NR 216 code, dated July 2004, and effective August 1, 2004.

The WWTP is a “treatment works treating domestic sewage”, and, as a Tier 2 facility, is required to obtain an Industrial Stormwater Discharge Permit [NR 216.21(2)b2] and complete a SWPPP.

## Objectives and Scope of Stormwater Pollution Prevention Plan

The SWPPP identifies potential sources of stormwater contamination, response and preventive measures utilized to reduce the risk of stormwater contamination, and ongoing management practices designed to prevent stormwater pollution at the subject facility.  It complies with the provisions of the Wisconsin Pollutant Discharge Elimination System (WPDES) stormwater permitting requirements outlined in the NR 216.

The SWPPP focuses on two major objectives:  (1) the identification of site activities that are potential sources of stormwater pollution; and (2) the identification of practices that minimize and control pollutants in stormwater runoff.

The scope of this plan includes:

Identifying Stormwater Team Coordinator and team members

Descriptions and maps showing applicable site features

An inventory of equipment used or stored at the facility

A description of exposed significant material

A list of significant spills and leaks over the last 3 years

A list of pollutant sources

A description of current and proposed Best Management Practices (BMPs)

Implementation schedule for BMPs

Employee training documentation

A description of site compliance and monitoring

Recordkeeping and internal reporting requirements

## Stormwater Pollution Prevention Responsibility

The Acting Director of Utilities, listed below, is responsible for all aspects of the Stormwater Management Program at the WWTP, including revisions to the SWPPP.

Chris Shaw

Acting Utilities Director

City of Appleton

2006 East Newberry Street

Appleton, Wisconsin 54911

(920) 832-2353

A Stormwater Pollution Prevention Team is responsible for implementation of this SWPPP.  Team members are as listed on Table 1 and described in Section 2 of this SWPPP.

## Plan Availability

A copy of this SWPPP is to be maintained at the WWTP at all times and will be made available to USEPA and WDNR representatives at their request.  A copy will also be kept at the City of Appleton’s Engineering Department.

## Plan Compliance and Modifications

This SWPPP will be updated and amended whenever there is a change in design, construction, operation, or maintenance that may impact the potential for pollutants to be discharged through stormwater.  This SWPPP also should be revised in accordance with the findings and recommendations of the annual Comprehensive Site Compliance Evaluation.  In addition, if this SWPPP is found to be ineffective in controlling the discharge of pollutants, the SWPPP is required to be amended to correct the identified deficiencies.

If the WDNR provides notification that the SWPPP does not meet the minimum requirements of the WPDES Stormwater Permit or NR 216 after an inspection of the facility and SWPPP, then the SWPPP must be modified accordingly within 30 days, and written certification that the changes were made must be provided to WDNR.

## Previously Developed Stormwater Management Plans

Certain other environmental management plans may contain provisions for managing stormwater.  In some cases, it may be possible to build on elements of these plans that are relevant to stormwater pollution prevention.

No other stormwater management plans were developed for the subject site to date.

# Stormwater pollution prevention team

The Stormwater Pollution Prevention Team consists of a team coordinator and team members who are assigned various responsibilities for implementing the SWPPP.  Implementation of this SWPPP includes ongoing assessment of potential sources of contamination and associated BMPs, response to spill events, if any, employee training, and the annual plan evaluation.  The current team roster is provided in Table 1.

## Team Coordinator

The Stormwater Pollution Prevention Coordinator has the ongoing responsibility for implementation of this SWPPP.  Specifically, this includes implementation of inspection schedules, records preservation, coordinating responses to spill emergencies, employee training, and annual updates to the SWPPP, if required.  The team coordinator serves as a point of contact for facility personnel and for those outside the facility (such as regulatory officials) who may wish to discuss aspects of the SWPPP or to obtain other information.  The coordinator oversees the re-evaluation and modification of the SWPPP annually and following a potential major spill event.  These modifications may include relocation or alteration of material storage or handling areas, BMP revisions, altering drainage patterns, addition of structural control measures, or documentation of significant leaks or spill events.  The coordinator must be familiar with all phases of facility operation to evaluate potential sources of pollution during implementation and periodic reevaluation of the SWPPP.

If a new team coordinator is assigned, the City of Appleton’s Utilities Director will make the selection.

## Team Members

Members of the team have the responsibility for conducting inspections, implementing and maintaining BMPs, conducting annual employee and new employee training, and responding to spill events, if any.  Pollution prevention team members will meet with the coordinator annually and following spill events to reevaluate and modify the SWPPP as needed.  If individual team members are replaced, equally qualified personnel will be assigned by the team coordinator to assume the previous member’s responsibilities.  If this cannot be accomplished immediately, the current team members will be assigned to those responsibilities during the interim.

TABLE 1

STORMWATER POLLUTION PREVENTION TEAM

WASTEWATER TREATMENT PLANT

APPLETON, WISCONSIN

(UPDATED JANUARY 6, 2017 BY APPLETON UTILITIES)

The following individuals make up the Stormwater Pollution Prevention Team for the Appleton Wastewater Treatment Plant, City of Appleton, Wisconsin.  Each member has specific responsibilities in maintaining and implementing the Stormwater Pollution Prevention Plan.  Individuals may have more than one responsibility.

| Responsibility | Name | Phone Number |
| --- | --- | --- |
| Team Coordinator | Brian Kreski | 920-832-2316 |
| Primary Emergency Contact (7:00 am – 3:30 pm M-F) | Brian Kreski | 920-832-2316 |
| Secondary Emergency Contact (7:00 am – 3:30 pm M-F) | Mike Suha | 920-832-2356 |
| Signatory | Chris Shaw | 920-832-2353 |
| Plan Implementation | Chris Shaw | 920-832-2353 |
| Plan Revision | Brian Kreski | 920-832-2316 |
| Employee Training | Brian Kreski | 920-832-2316 |
| Inspections | Brian Kreski | 920-832-2316 |
| Preventive Maintenance | Brian Kreski | 920-832-2316 |
| Spill Response | Brian Kreski | 920-832-2316 |
| After Hours Emergency Service (3:30 pm – 7:00 am M-F; All day Sat. & Sun.) | Mactel | 920-730-3004 |

# potential contamination sources and risk identification

## Initial Site Evaluation Summary

The site evaluation includes an assessment of potential pollutant sources to determine areas, activities, and materials that may contribute pollutants to stormwater runoff.  The evaluation determines the necessity for BMPs and helps guide the selection of the most appropriate BMPs to prevent or control pollutants from these areas, activities, and materials.

Earth Tech, Inc. (Earth Tech) conducted an initial site evaluation on September 29, 2003, and subsequent visits were made in October 2004 and on April 12, 2005.  Observations made during these visits are:

- Utilities vehicles are occasionally parked outdoors, however, no equipment maintenance activities are conducted outdoors

- Solid waste and recycling collection containers were adequately covered, and appeared to be watertight

- The parking area consists of bituminous asphalt

- The vegetated areas of the Site help to prevent erosion and filter stormwater.

No staining, pools, puddles, or other evidence of oils, greases, or other chemicals were observed on the facility surface.

Earth Tech identified areas potentially exposed to stormwater based upon stormwater flow and area usage.  These areas are:

Asphalt drives and parking areas

Refuse and recycling containers

Fuel oil and gasoline storage tanks

Outdoor salvage material storage area

Electrical substation

Wastewater treatment processes

Chemical unloading area

## Stormwater Drainage and Outfalls

There are seven stormwater drainage basins at the WWTP site.  Figure 2 identifies the drainage basins, overland flow patterns, buildings, drainage structures, surface material, and site use.  Table 2 lists the drainage basins and the corresponding areas, activities, uses, and impervious area.

Basins 1 through 6 include the wastewater treatment facilities complex.  Runoff generally enters stormwater inlets and is discharged back to the plant or to the Fox River (Outfalls 1, 2, 3, and 4 shown on Figure 2), flows overland by sheet flow to the Fox River, or runs off to the surrounding grassed areas.

Basin 7 includes the paved access drive and mostly grassed areas.  Runoff infiltrates into the soil or flows off-site to vegetated areas.

Based upon the drainage plan for the WWTP, the flow direction of all storm sewers on site cannot be determined.  It appears that there is some flow directly to the plant and some flow to the outfalls into the Fox River.  A full survey and mapping of the system is recommended with dye testing to determine the flow directions in the storm sewer system.  WDNR must be notified prior to conducting any dye testing of the storm sewer system at the WWTP.

TABLE 2

Stormwater AREAS AND ACTIVITY INVENTORY

WASTEWATER TREATMENT FACILITY

APPLETON, WISCONSIN

| Area ID. | Area Drained (square feet) | Percent Impervious | Area Activities |
| --- | --- | --- | --- |
| 1 | 856,000 (19.6 acres) | 50% See Note | Wastewater treatment processes; refuse and recycling containers; equipment and vehicle parking areas; chemical unloading area; fuel storage and dispensing; salvage material storage; grassed areas. |
| 2 | 7,700 (0.2 acres) | 50% See Note | Wastewater treatment processes; paved drives; grassed areas. |
| 3 | 128,000 (2.9 acres) | 80% See Note | Wastewater treatment processes; paved drives; grassed areas. |
| 4 | 256,000 (5.9 acres) | 30% See Note | Wastewater treatment processes; paved drives; grassed areas. |
| 5 | 73,000 (1.7 acres) | 75% See Note | Wastewater treatment processes; paved drives; grassed areas. |
| 6 | 8,700 (0.2 acres) | 100% | Chemical unloading area; paved drives. |
| 7 | 563,000 (12.9 acres) | 2% | Paved entrance drive; grassed areas. |

Note:  Precipitation that falls into open wastewater treatment units is not considered stormwater

## Areas of Potential Stormwater Contamination

### Asphalt Drives and Parking Areas

These features are within all seven basins of the WWTP (see Figure 2).  Stormwater enters inlets or sheet flows onto vegetated areas beyond the pavement, where it discharges off-site.

Inventory of Exposed Materials/Risk identification

- Equipment and vehicles in these areas are exposed to precipitation.  Traffic includes customer, vendor, and employee vehicles as well as Utilities’ equipment.

- These areas have the potential to contribute solids, salt, and oil and grease from vehicles that may leak during transit, as well as from parked vehicles and equipment.  There is a small potential for wastewater treatment chemicals to be spilled in Basin 1 during unloading activities.

- Potential pollutant parameters:  total suspended solids (TSS), total dissolved solids (TDS), chemical oxygen demand (COD), total oil and grease (TOG), and chlorides.

### Refuse and Recycling Containers

The refuse and recycling containers are located north of the S-Building in Basin 1.  The recycling area contains recycling bins for plastics, metals, and other recyclable materials.  This entire area is paved.  Stormwater runoff from this area sheet flows on the asphalt to local inlets.

Inventory of Exposed Materials/Risk Identification

- The refuse and recycling containers are not under roof and are exposed to precipitation.

- Potential pollutant parameters: TSS, TDS, COD, pH, and TOG.

### Fuel Oil and Gasoline Storage Tanks

The fuel storage tanks (diesel and unleaded gasoline) used to fuel Utilities’ vehicles are located east of the V-Building near the electrical substation.  Stormwater runoff from this area sheet flows on the asphalt to the inlets in Basin 1, or into grassed areas.

- The fuel tanks and fueling area are not under roof and are exposed to precipitation.

- The potential exists for debris to be carried off the asphalt drive and enter the nearby stormwater inlets.

- The fueling of vehicles can occasionally result in small spills of fuel that are expected to cause impacts to stormwater.

- Potential pollutant parameters: TSS, TDS, COD, pH, Diesel-Range Organics (DRO), Gasoline-Range Organics (GRO), and TOG.

### Equipment and Material Storage Areas

There is a dedicated equipment and salvage materials storage area located on an unpaved surface southeast of the V-2 Building in Basin 1.  The material stored at that location includes items such as tanks, piping, and miscellaneous used equipment.  In addition, soils from construction activities may be stockpiled in the area.  Stormwater runoff sheet flows on the grassed surface to the drainage swale that runs north toward the Fox River.

Inventory of Exposed Materials/Risk Identification

- Most of the materials stored in this area are inert such as plastic tanks and piping.   Some of the metal materials stored in this area have the potential to rust and impact stormwater.

- The area has the potential for misplaced materials to contaminate stormwater, especially spilled oil and other liquids from vehicles and equipment.

- Potential pollutant parameters: TSS, TDS, COD, and TOG.

### Electrical Substation

The electrical substation is located south of Building L in Basin 1.  Stormwater runoff sheet flows on the asphalt to the inlets, or onto grassed areas.

Inventory of Exposed Materials/Risk Identification

- The electrical substation is not under roof and is exposed to precipitation.

- Potential pollutant parameters:  TOG, TSS, TDS.

### Sewage Unloading Areas

The waste receiving station is located on the east side of Building L in Basin 1.  Trucks deliver waste and sewage to indoor storage tanks via outside fill ports.  Surface drainage flows across the pavement to stormwater inlets, or onto grassed areas.  The delivery area is depressed and can hold up to 5,000 gallons in the event of a spill.

Inventory of Exposed Materials/Risk Identification

- The receiving area is exposed to precipitation.

- The potential exists for contaminants to be carried off the pavement and onto the adjacent grassy areas.

- Potential pollutant parameters:  TSS, TDS, DRO, COD.

### Chemical Unloading Areas

Chemical unloading occurs in three separate locations.  Trucks deliver wastewater treatment chemicals to indoor chemical storage tanks via outside fill ports located on the west side of F-2 Building in Basin 6.  Surface drainage flows across the pavement to stormwater inlets and then via pipe to the headworks of the plant, or via surface drainage to the Fox River.  The chemical unloading area is depressed and can hold up to 5,000 gallons in the event of a spill.  Trucks also deliver wastewater treatment chemicals to indoor chemical storage tanks via fill ports located inside L and V Buildings.  No outside chemical unloading occurs in these two areas.

Inventory of Exposed Materials/Risk Identification

- The unloading area adjacent to F-2 Building is exposed to precipitation.

- There is a potential for contaminants to be carried off the pavement and into the Fox River.

Potential pollutant parameters:  TSS, TDS, DRO, COD, and ferrous sulfate.

## Materials Inventory

Materials that are managed at this facility with potential to contribute to stormwater pollution are itemized on Table 3.  These materials are identified by the material description, use, location, approximate quantity of material used, containment methods, and likelihood of exposure to stormwater.

## Historical Leaks and Spills

Based on information provided by City of Appleton staff, no reportable quantity leaks or spills have occurred at the facility within the last 3 years.  From inspection during the site visit, no evidence was found of any leaks or spills discharging off-site.

TABLE 3

MATERIALS INVENTORY

WASTEWATER TREATMENT FACILITY

APPLETON, WISCONSIN

| Material Description | Material Use | Location | Approximate Quantity | Containment Methods | Likelihood of Exposure to Stormwater |
| --- | --- | --- | --- | --- | --- |
| Refuse and Recycling Containers | Refuse and Recyclable Material Collection | On Pavement North of S-Building in Basin 1 | Up to 5 containers of various size | None | Likely, however, minimal impacts expected because containers are covered, and inspected daily. |
| Wastewater Treatment Chemicals | Chemical Unloading Areas | Adjacent to F2, L, and V-Buildings in Basin 1 | All Chemical Storage Tanks Inside. F2-Building: 4 @ 5,000 gal Ferrous Sulfate L-Building: 1 @ 3,200 gal and 2 @ 2,000 gal polymer 1 @ 2,900 gallon sodium bisulfate 2 @ 8,600 gal sodium hypochlorite V-Building: 2 @ 4,220 gal and 3 @ 2,000 gal polymer | Secondary containment for unloading areas and inside for tanks. | Unlikely, because any spills are cleaned up immediately. |
| Fuel Oil and Gasoline | Process and Vehicle Fuels | East of V-Building (vehicle) | Vehicle: 1 @ 1,000 gal diesel and 1@500 gal gasoline | Double-wall tanks (all) | Likely, however, minimal impacts expected because fueling protocols include spills management and reporting. |
| Salvage and Materials Storage | Temporary Storage of Materials | Southeast of V-2 Building | Variable | None | Likely, however, minimal impacts expected because only clean and inert materials are stored in this location. |
| Utilities Employees and Customer Vehicles | Outside Parking | On Pavement in Basins 1 and 2 | Variable, up to 30 vehicles | None | Likely, however, minimal impacts expected because Utilities vehicles are kept clean and inspected regularly. |

# non-stormwater discharges

Portions of this facility are serviced by a municipal storm sewer system and portions are serviced by an on-site private storm sewer system.  Earth Tech initially conducted an evaluation for the presence of non-stormwater discharges, through on-site observations and discussion with site personnel on September 29, 2003.  No non-stormwater discharges were identified during the site reconnaissance.

SWPPP requirements include a certification, signed by an authorized individual that the provisions of the SWPPP will be adhered to.  This includes an understanding that stormwater discharges from the site have been tested or evaluated for the presence of non-stormwater discharges.

# BEST MANAGEMENT PRACTICES

## Objective

This section describes BMPs for general facility operations and for each of the potential areas of stormwater contamination.  The primary objective of BMPs is to prevent stormwater from coming into contact with source materials.  Wherever possible, sources will be removed or covered to eliminate stormwater contamination.  If source controls are inadequate, treatment practices may be recommended.

This section includes measures and controls taken to promote good housekeeping, run-on/runoff management and preventive maintenance.  Spill prevention techniques, inspections, employee training, and recordkeeping are addressed in separate sections of this SWPPP.

## Measures and Controls

Activities and materials present at the WWTP that may cause potential impacts to stormwater discharges are listed in Section 3.3 and summarized on Table 3.

The City of Appleton understands that source control is the most effective way to reduce pollutants in stormwater.  Measures such as removing wastes, storing materials inside, and establishing a waste removal schedule that minimizes on-site storage have been implemented wherever possible.  A summary of existing and proposed control measures follows.

### Existing BMPs

Existing Stormwater Management Practices that will be continued include:

E1	A large area of the property is maintained in a vegetated condition.  This area serves as a filtering media for stormwater runoff.

E2	The amount of vegetation chemically treated for weeds is kept to a minimum.

E3	Equipment and vehicles parked on the property are properly cleaned and maintained so that they do not have contaminants exposed to rainfall.  Drip pans are used to collect contaminants if any leaks occur.

E4	No vehicle maintenance or washing occurs outdoors at the WWTP.

E5	The dumpsters and recycling bins have covers, drains are plugged, and they are inspected frequently.

E6	Standard procedures for loading and unloading chemicals include constant attendance and immediate cleanup of any spills.

E7	The site is neatly maintained and good housekeeping standards are followed.

E8		Chemical storage, piping and dispersing systems are located inside of the building.

E9		Spill kits are located near the fuel storage tanks.

### Proposed BMPs (Updated to Existing BMPs)

Implementation of the following BMPs will minimize stormwater contamination:

E10	Continue to maintain the existing BMPs.

E11	Continue to maintain good housekeeping standards at all times.

E12	Conduct quarterly visual stormwater inspections and annual facility site inspections.  The quarterly visual inspection will consist of observing stormwater runoff from each of the outfalls identified in this SWPPP and from each area where activities have the potential to impact stormwater.

E13	Implement an employee-training program (Refer to Section 6.7).

E14	Any equipment or other items that are temporarily stored outdoors should be evaluated for potential contaminants.  If it is determined that the items include potential contaminants (e.g., oil, grease, particulates) that would be exposed to rainfall and could enter the stormwater runoff, consideration should be given to properly protecting the item, removing the potential contaminants, or storing the item indoors until the item can be stored or disposed properly.

E15	Conduct routine inspections of the fuel storage area, the drives and parking areas.

E16	All spills shall be promptly cleaned up.  Cleanup may involve shoveling or sweeping the solids, or using commercial sorbent material to absorb oil and grease spills.  Any reportable spill must be reported to the WDNR, the Appleton Fire Department and the Utilities Director.  A summary of Wisconsin Spill Reporting Requirements is included in Appendix D.

E17	Use minimum amount of de-icing salt needed to maintain safe conditions.  Consider using a sand and salt mixture.

E18	Require chemical suppliers to provide spill plans for delivery and documentation of spill prevention training for drivers.

E19	A fertilizer management plan, following state guidelines and city ordinance, will be developed for the appropriate application of fertilizers and pesticides on the site.

E20	Map the storm sewer system.

## Best Management Practices Implementation

The existing BMPs will continue to be followed or maintained.  Proposed BMPs will be implemented within 24 months of the effective date of coverage under the permit, in accordance with NR 216.29(5).  If future changes in operational activities at the WWTP require the implementation of additional BMPs, this plan will be modified accordingly.

The existing and proposed BMPs are outlined in Table 4.

TABLE 4

RECOMMENDED BEST MANAGEMENT PRACTICES

WASTEWATER TREATMENT FACILITY

APPLETON, WISCONSIN

(UPDATED JANUARY 6, 2017 BY APPLETON UTILITIES)

| Status | Best Management Practices | Description of Activity |
| --- | --- | --- |
| Existing to be continued | E1, E2 | The amount of grass and/or brush treated with herbicide and fertilizer is kept to a minimum. |
| Existing to be continued | E3, E4, E7 | The Site is neatly maintained. Well-maintained Utilities vehicles may be temporarily parked outdoors. |
| Existing to be continued | E5 | Refuse and recycling bins are covered to properly protect from rainfall. |
| Existing to be continued | E9 | Continue to stock materials, supplies, and equipment for managing fuel spills. |
| Existing to be continued | E8 | Chemical storage and piping are located inside buildings. |
| Existing to be continued | E6 | SOPS are followed for loading chemicals product to the storage tanks in order to minimize the potential for spills. |
| Existing to be continued | E10 | Adjust deicer usage in accordance with activities. Sweep residual salts regularly during salt season, and again in Spring. Sweep any other accumulations of sediment as needed. Any observed leak or spill will be contained, cleaned up, and responded to promptly. |
| Existing to be continued | E19 | A fertilizer management plan will be developed for the facility. |
| Existing to be continued | E16, E9 | Purchase spill kits and store at locations readily accessible to employees and drivers of the bulk chemical delivery trucks. Replenish spill supplies as needed. |
| Existing to be continued | E15 | Remove items from the outside storage area that may have the possibility of contaminated stormwater. |
| Existing to be continued | E10, E11 | Maintain existing BMPs and good housekeeping standards. |
| Existing to be continued | E18 | Require chemical suppliers to have spill plans for deliveries. |
| Status | Other Practices | Description of Activity |
| Existing to be continued | E12, E15 | Property is routinely inspected. Quarterly and annual site evaluations will be performed. |
| Existing to be continued | E13 | Annual meetings will be held to address health, safety, and spill prevention and response. |
| Existing to be continued | E10, E11, E12, E13, E15, E16, E20 | Records will be kept and maintained for spills, inspections, and maintenance activities. This SWPPP will be updated any time there is a change in the potential for pollutants to enter storm water, when pollution prevention practices change, or if the plan is ineffective in preventing storm water pollution. Records will be retained for a period of 5 years. |

## Prohibited Activities

The following are prohibited activities:

Spraying or applying liquids onto pavements or gravel areas of the facility where they would discharge along with stormwater.

Washing or maintaining vehicles outside.

The cleaning of spills by flushing with water, unless the mapping of the storm sewer system indicates the stormwater flows to the plant for treatment.  If the stormwater does not go to the plant for treatment, then spills and sediments are to be cleaned-up by using absorbent material or sweeping.

## Residual Pollutants Expected to Remain in Stormwater

Based on current operations at the subject site and the anticipated implementation of the BMPs, low concentrations of residual pollutants that are expected to remain in stormwater include TOG from employee/visitor parking areas, TSS from motor vehicle traffic, residual chemicals from unloading areas and filling operations, and calcium chloride for snow and ice control.  Implementation of this SWPPP and the BMPs are believed to be adequate to minimize most known or unknown pollutants in the facility’s stormwater runoff.

## Stormwater Treatment Practices

The BMPs described above are appropriate for the activities that occur at this Site.  TSS will still be discharged from the Site in untreated stormwater runoff.  Some Stormwater Treatment Practices (STP) that may be appropriate for the site to reduce TSS discharges include diversion channels (swales) and vegetative filters.  These and other potential STPs should be evaluated and incorporated into this SWPPP if they can achieve cost-effective sediment removal.

# inspections and recordkeeping

Quarterly inspections must be conducted to document that the provisions of this SWPPP are being followed and to identify areas, if any, needing improvement.  Deficiencies revealed during inspection procedures that require further action, such as purchasing or replacing equipment should be communicated to the SWPPP team coordinator.  Blank forms are located in Appendix B and completed forms are placed in Appendix C.  Inspection records must be retained for a period of at least 5 years.

## Quarterly Visual Stormwater Inspections

Each outfall should be inspected at least once every three months during a rainfall event.  Each inspection must be conducted within the first 30 minutes or as soon thereafter as practical, but not to exceed 60 minutes, after runoff begins discharging to an outfall or leaving the property.  The inspections should be documented, and include observations of color, odor, clarity, floating solids, foam, oil sheen, or other obvious indicators of stormwater pollution.

## Annual Site Inspection

A comprehensive annual facility site compliance inspection (AFSCI) must be performed.  These inspections will be used to verify that the site drainage conditions and potential pollutant sources identified in the SWPPP remain accurate, and that the BMPs prescribed in the SWPPP are being implemented.  The findings from the annual inspection must be documented.  Based on the findings from these inspections, the WWTP’s SWPPP may need to be revised.  A blank WDNR AFSCI Form No. 3400-176 is enclosed in Appendix B.  A thorough inspection, together with information from the quarterly and semi-annual dry weather inspection checklists, should be used to complete this form.  The WDNR AFSCI form must be completed and retained by the facility.  The completed forms do not need to be mailed to the WDNR.

A site-specific annual inspection checklist is included in Appendix B.  This checklist can be completed as an attachment to the WDNR AFSCI Form 3400-176A, if desired.

## Semi-Annual Dry Weather Inspection

Semi-annual visual observations, during dry weather, must be completed at each outfall of the storm sewer collection system.  Observations shall be made at times when non-stormwater discharges from the facility are considered most likely to occur (i.e., periods of dry weather during normal working hours).  Indications of stains, sludges, color, odor, or other indications of a non-stormwater discharge shall be recorded on the Non-Stormwater Discharge Assessment and Certification.  In addition, an authorized representative of the facility must sign a certification statement on each inspection form indicating that the information on the form is accurate and complete.  A copy of these completed forms must be retained by the facility.

## Spill Management and Documentation

Should a spill occur in an area on the property that could be exposed to stormwater, the spill must be cleaned up immediately.  If the spill is reportable, it must be reported to the WDNR, the Appleton Utilities Director and the Appleton Fire Department.

A record should be kept of all spills, and should include the following:

Date and time of the incident

Substance spilled

Volume spilled

Weather conditions

Duration of the incident

Cause of the incident

Response procedures

Parties notified

Amount of spilled material recovered and recovery method

A spill documentation form is enclosed and should be used to record the pertinent data that must be documented whenever a spill occurs.  A brief WDNR fact sheet providing definition for a reportable spill is included in Appendix D.

## Annual Stormwater Sampling and Testing

The City of Appleton is not required to collect stormwater samples at the WWTP for analytical testing because it is not a Tier 1 facility per NR 216.21(2)a.

## SWMP Updates or Revisions

The facility must amend their SWPPP whenever there is a change in pollution prevention team personnel, or facility design, construction, or operation that may impact the potential for pollutants to come into contact with stormwater, or if the SWPPP proves to be ineffective in controlling the discharge of pollutants.

## Employee Training Requirements

To effectively implement the SWPPP, employees must be adequately trained.  The goal of the training program is to teach personnel the components and goals of the pollution prevention plan.  Properly trained personnel can recognize situations that could contaminate stormwater and can respond safely and effectively to an accident.  The employee training program should cover topics such as:

Spill prevention and response

Good housekeeping

Material management practices

All employees should be trained at least annually.  Training frequency should be determined based upon the complexity of stored materials, stormwater management practices, staff turnover, and changes in job assignments at the facility.  Training effectiveness should be evaluated to ensure information has been effectively communicated.  An employee training record is included in Appendix B.

## Preventive Maintenance

WWTP staff should perform preventive maintenance checks on all stormwater management devices (e.g., catch basins, or other structural or treatment management practices) used at the facility.  These devices and management practices should be examined during the quarterly visual stormwater inspections, or more frequently if needed.  The contents of the spill kits should be checked during the quarterly inspections and after each use.  Spill equipment should be replaced as needed.

## Implementation Schedule

The WWTP must complete a SWPPP within 12 months after the issue date of their stormwater permit.  The SWPPP implementation schedule is shown in Table 5.

TABLE 5

SWPPP IMPLEMENTATION SCHEDULE

WASTEWATER TREATMENT PLANT

APPLETON, WISCONSIN

| SWPPP Element | Implementation Date |
| --- | --- |
| *Submit SWPPP Summary to WDNR | Within 12 months from the effective date of permit coverage. |
| Implement BMPs | Within 24 months from the effective date of permit coverage. |
| Conduct quarterly visual inspections | Quarterly - beginning within 24 months of permit coverage. |
| Conduct annual facility site compliance inspection | Annually - beginning within 24 months of permit coverage. |
| *Prepare annual site inspection report | Annually by March 31 beginning within 24 months of permit coverage. |

Implementation of this schedule was December 15, 2006

*Submit only on request from WDNR.

# references

United States Environmental Protection Agency, Stormwater Management for Industrial Activities - Developing Pollution Prevention Plans and Best Management Practices, September 1992.  EPA 832-R-92-006.

Wisconsin Department of Natural Resources, The Wisconsin Stormwater Manual, Bureau of Water Resource Management, Non-point Source and Land Management Section, Publication Number:  WR-349-94.

Wisconsin Department of Natural Resources, Wisconsin’s Guidance for Industrial Stormwater Sampling, Bureau of Wastewater Management, Municipal Wastewater Section - Stormwater Unit, September 1994.

U.S. Department of Labor, Occupational Safety and Health Administration, "Standard Industrial Code Manual", 1987.

FIGURES

Appendix  A

General Industrial Stormwater Permit

Appendix  B

Blank Checklists and Forms

Appendix  C

Completed Checklists and Forms

Appendix  D

WDNR Fact Sheet

Defining Reportable Spills